## LineRating_IEEE
IEEE 738 - 2006 Example calculation
Steady State Heat Balance Equation
| I | Conductor Current |  |  | Natural Convection Heat Loss(Qcn) |  |  | Radiated Heat Loss(Qr)
| Qc | Convection Heat Loss |  |  | T(film) | 70 |  | Qr | 9.0565
| Qr | Radiated Heat Loss |  |  | Air Density(pf)(lb/ft^3) | 0.063448
| Qs | Solar Heat Gain |  |  | Qcn(W/ft) | 14.8667
| Tc | Conductor Temperature | [5 empty] | Solar Heat Gain (Qs)
[5 empty] | Forced Convection Heat Loss Rate(Qc1,Qc2) |  |  | N | 161
[5 empty] | Qc1 | 27.437 |  | δ | 23.0198
[5 empty] | Qc2 | 26.12 |  | Hc | -11.7129
[8 empty] | ω | -120
[5 empty] | Dynamic Viscosity of Air |  |  | Zc | 54.49
[5 empty] | μf | 0.049458 |  | X | 1.4014 | Hour Angle ω (degrees) | C if X >= 0 (degrees) | C if X<0 (degrees)
Input |  |  |  |  | Thermal Conductivity of Air |  |  | C | 0 | -180<=ω<0 | 0 | 180
Conductor | 1272 ACSR (BITTERN) |  |  |  | Kf | 0.0089767 | W/(ft-C) | Qs Clear | -3.5502 | 0<=ω<=180 | 180 | 360
Wind Speed (Vw)(ft/s) | 2 | 7200 | Vw |  | Wind Direction Factor |  |  | Qs Industrial | -0.0031953
Emissivity(ɛ) | 0.5 |  | ɛ |  | Kangle | 1 |  | θ | 37.1494 | Clear Atmosphere
Solar Absorpivity(a) | 0.5 |  | a |  |  |  |  | Qse Clear | -104.9032 | A | -3.9241
Ambient Air Temp (C) | 40 | 104 | Ta |  | Convection Heat Loss Final (Qc) |  |  | Qse Industrial | 3.7236 | B | 5.9276
Max Allowable Conductor Temp (C) | 100 | 212 | Tc |  | Qc | 27.437 |  | Ksolar | 1.0116 | C | -0.17856
Conductor Outside Diameter (inches)(ft) | 1.345 | 0.11208 | D A' |  |  |  |  | Qs Sea Level Clear | -103.7016 | D | 0.003223
Conductor AC Resistance R(25C)(Ω/ft) | 1.5758e-05 | 2.22e-05 | R(Tc) | 25 | Resistance at 100 degrees C |  |  | Qs Sea Level Industrial | 3.681 | E | -3.3549e-05
Conductor AC Resistance R(75C)(Ω/ft) |  | 2.648e-05 | R(Tc) | 75 | R(Tc) | 2.862e-05 |  |  |  | F | 1.8053e-07
Azmith of Line (Z) | 90 |  | Zl |  | Conductor Temp for c | 100 |  |  |  | G | -3.7868e-10
Lattitude | 30 | North | Lat | [6 empty] | Industrial Atmosphere
Atmosphere | Clear | [6 empty] | 0 | -180 | A | 4.9408
Date/Time | 2015-06-10 | 4 | 11 |  | Answer |  |  | 1 | -165 | B | 1.3202
Average Conductor Elevation (ft)(m) | 328 | 99.9744 | He |  | 1182.8567 |  |  | 2 | -150 | C | 0.061444
[8 empty] | 3 | -135 | D | -0.0029411
Wind Direction Angle(degrees) | 0 |  | ϐ |  |  |  |  | 4 | -120 | E | 5.0775e-05
Atmosphere | Qs Clear | -3.5502 | [5 empty] | 5 | -105 | F | -4.0363e-07
[8 empty] | 6 | -90 | G | 1.2297e-09
[8 empty] | 7 | -75
[8 empty] | 8 | -60
[8 empty] | 9 | -45
[8 empty] | 10 | -30
[8 empty] | 11 | -15
[8 empty] | 12 | 0
[8 empty] | 13 | 15
[8 empty] | 14 | 30
[8 empty] | 15 | 45
[8 empty] | 16 | 60
[8 empty] | 17 | 75
[8 empty] | 18 | 90
[8 empty] | 19 | 105
[8 empty] | 20 | 120
[8 empty] | 21 | 135
[8 empty] | 22 | 150
[8 empty] | 23 | 165
[8 empty] | 24 | 180
𝐼=√(𝑞𝑐+𝑞𝑟−𝑞𝑠)/(𝑅(𝑇𝑐))

## ConductorData
STATIC | NAME | GMR(ft) | RADIUS(ft) | RATEA(A) | RATEB(A) | RATEC(A) | R(Ohms/mi) | XL(Ohms/mi) | XC(Ohms-mi) | Type | Code | Name
0 | 1272 | 0.0455 | 0.05604 | 1190 | 1276.2 | 1579.5 | 0.0832 | 0.378 | 0.0855 | ACSR | BITTERN | 1272 ACSR (BITTERN)
0 | 1351.5 | 0.0459 | 0.0589 | 1235.7 | 1325.7 | 1642.5 | 0.0803 | 0.369 | 0.0838 | ACSR | DIPPER | 1351.5 ACSR (DIPPER)