## ACSR Table 1-29
TABLE 1-29
Aluminum Conductor, Steel Reinforced (ACSR)
Code Word | Conductor Size (kcmil) | Stranding (Al/St) | Cross-Sectional Area - Aluminum (in^2) | Cross-Sectional Area - Total (in^2) | Layers of Al | Diameter - Aluminum Strands (in) | Diameter - Steel Strands (in) | Diameter - Steel Core (in) | Diameter - Complete Conductor (in) | Weight/1000 ft - Aluminum (lb) | Weight/1000 ft - Steel (lb) | Weight/1000 ft - Total (lb) | Metal Content - Aluminum (%) | Metal Content - Steel (%) | RBS (lb) | Resistance dc @ 20°C (Ω/mile) | Resistance ac @ 25°C (Ω/mile) | Resistance ac @ 50°C (Ω/mile) | Resistance ac @ 75°C (Ω/mile) | GMR (ft) | Reactance Inductive Xa (Ω/mile) | Reactance Capacitive X'a (MΩ-mile) | Ampacity @ 75°C (amp)
Waxwing | 266.8 | 18/1 | 0.2094 | 0.221 | 2 | 0.1217 | 0.1217 | 0.1217 | 0.609 | 249.9 | 39.2 | 289.1 | 86.4 | 13.6 | 6880 | 0.3396 | 0.3471 | 0.3813 | 0.4155 | 0.0197 | 0.477 | 0.109 | 449
Partridge | 266.8 | 26/7 | 0.2095 | 0.2436 | 2 | 0.1013 | 0.0788 | 0.2364 | 0.642 | 251.3 | 115.6 | 366.9 | 68.5 | 31.5 | 11300 | 0.3364 | 0.3437 | 0.3775 | 0.4113 | 0.0217 | 0.465 | 0.1074 | 457
Junco | 266.8 | 30/7 | 0.2095 | 0.2584 | 2 | 0.0943 | 0.0943 | 0.2829 | 0.66 | 251.9 | 165.5 | 417.4 | 60.3 | 39.7 | 13900 | 0.3342 | 0.3413 | 0.3748 | 0.4083 | 0.0227 | 0.459 | 0.1066 | 462
Ostrich | 300 | 26/7 | 0.2355 | 0.2738 | 2 | 0.1074 | 0.0835 | 0.2505 | 0.68 | 282.5 | 129.7 | 412.2 | 68.5 | 31.5 | 12700 | 0.2992 | 0.3058 | 0.3358 | 0.3659 | 0.023 | 0.458 | 0.1057 | 492
Merlin | 336.4 | 18/1 | 0.2642 | 0.2789 | 2 | 0.1367 | 0.1367 | 0.1367 | 0.684 | 315.3 | 49.5 | 364.8 | 86.4 | 13.6 | 8680 | 0.2693 | 0.2756 | 0.3027 | 0.3298 | 0.0221 | 0.463 | 0.1056 | 519
Linnet | 336.4 | 26/7 | 0.264 | 0.307 | 2 | 0.1137 | 0.0884 | 0.2652 | 0.72 | 316.6 | 145.4 | 462 | 68.5 | 31.5 | 14100 | 0.2668 | 0.2728 | 0.2996 | 0.3264 | 0.0243 | 0.451 | 0.104 | 529
Oriole | 336.4 | 30/7 | 0.2642 | 0.3259 | 2 | 0.1059 | 0.1059 | 0.3177 | 0.741 | 317.7 | 208.7 | 526.4 | 60.3 | 39.7 | 17300 | 0.265 | 0.2708 | 0.2974 | 0.324 | 0.0255 | 0.445 | 0.1031 | 535
Chickadee | 397.5 | 18/1 | 0.3122 | 0.3295 | 2 | 0.1486 | 0.1486 | 0.1486 | 0.743 | 372.5 | 98.5 | 471 | 86.4 | 13.6 | 9940 | 0.2279 | 0.2336 | 0.2565 | 0.2794 | 0.024 | 0.452 | 0.1031 | 576
Ptarmigan | 397.5 | 20/7 | 0.3123 | 0.3339 | 2 | 0.141 | 0.0627 | 0.1881 | 0.752 | 374.5 | 13.2 | 387.7 | 83.7 | 16.3 | 11100 | 0.2286 | 0.2342 | 0.2571 | 0.2801 | 0.0246 | 0.45 | 0.1027 | 577
Brant | 397.5 | 24/7 | 0.3122 | 0.3527 | 2 | 0.1287 | 0.0858 | 0.2574 | 0.772 | 374.4 | 137 | 511.4 | 73.2 | 26.8 | 14600 | 0.2268 | 0.2321 | 0.2549 | 0.2777 | 0.0259 | 0.444 | 0.1019 | 584
Ibis | 397.5 | 26/7 | 0.312 | 0.3628 | 2 | 0.1236 | 0.0961 | 0.2883 | 0.783 | 374.1 | 171.9 | 546 | 68.5 | 31.5 | 16300 | 0.2258 | 0.2311 | 0.2537 | 0.2764 | 0.0265 | 0.441 | 0.1015 | 587
Lark | 397.5 | 30/7 | 0.3121 | 0.3849 | 2 | 0.1151 | 0.1151 | 0.3453 | 0.806 | 375.3 | 246.5 | 621.8 | 60.3 | 39.7 | 20300 | 0.2243 | 0.2294 | 0.2518 | 0.2743 | 0.0277 | 0.435 | 0.1007 | 594
Pelican | 477 | 18/1 | 0.3747 | 0.3955 | 2 | 0.1628 | 0.1628 | 0.1628 | 0.814 | 447.1 | 70.2 | 517.3 | 86.4 | 13.6 | 11800 | 0.1899 | 0.195 | 0.2141 | 0.2331 | 0.0263 | 0.441 | 0.1004 | 646
Tailorbird | 477 | 20/7 | 0.3745 | 0.4004 | 2 | 0.1544 | 0.0686 | 0.2058 | 0.824 | 449.1 | 87.6 | 536.7 | 83.7 | 16.3 | 13100 | 0.1905 | 0.1955 | 0.2146 | 0.2337 | 0.027 | 0.439 | 0.1 | 647
Flicker | 477 | 24/7 | 0.3747 | 0.4233 | 2 | 0.141 | 0.094 | 0.282 | 0.846 | 449.4 | 164.5 | 613.9 | 73.2 | 26.8 | 17200 | 0.189 | 0.1937 | 0.2127 | 0.2316 | 0.0283 | 0.433 | 0.0992 | 655
Hawk | 477 | 26/7 | 0.3744 | 0.4354 | 2 | 0.1354 | 0.1053 | 0.3159 | 0.858 | 449 | 206.4 | 655.4 | 68.5 | 31.5 | 19500 | 0.1882 | 0.1928 | 0.2117 | 0.2305 | 0.029 | 0.43 | 0.0988 | 659
Hen | 477 | 30/7 | 0.3747 | 0.4621 | 2 | 0.1261 | 0.1261 | 0.3783 | 0.883 | 450.4 | 296 | 746.4 | 60.3 | 39.7 | 23800 | 0.1869 | 0.1913 | 0.2101 | 0.2288 | 0.0304 | 0.424 | 0.098 | 666
Osprey | 556.5 | 18/1 | 0.4369 | 0.4612 | 2 | 0.1758 | 0.1758 | 0.1758 | 0.879 | 521.4 | 81.8 | 603.2 | 86.4 | 13.6 | 13700 | 0.1628 | 0.1676 | 0.1838 | 0.2002 | 0.0284 | 0.432 | 0.0981 | 714
Sapsucker | 556.5 | 22/7 | 0.4368 | 0.4797 | 2 | 0.159 | 0.0883 | 0.2649 | 0.901 | 523.9 | 145.1 | 669 | 78.3 | 21.7 | 17600 | 0.1627 | 0.1672 | 0.1834 | 0.1997 | 0.0298 | 0.426 | 0.0974 | 717
Parakeet | 556.5 | 24/7 | 0.4372 | 0.4938 | 2 | 0.1523 | 0.1015 | 0.3045 | 0.914 | 524.3 | 191.8 | 716.1 | 73.2 | 26.8 | 19800 | 0.162 | 0.1663 | 0.1826 | 0.1988 | 0.0306 | 0.423 | 0.0969 | 721
Dove | 556.5 | 26/7 | 0.4371 | 0.5083 | 2 | 0.1463 | 0.1138 | 0.3414 | 0.927 | 524.2 | 241 | 765.2 | 68.5 | 31.5 | 22600 | 0.1613 | 0.1655 | 0.1817 | 0.1978 | 0.0313 | 0.42 | 0.0965 | 725
Eagle | 556.5 | 30/7 | 0.4371 | 0.5391 | 2 | 0.1362 | 0.1362 | 0.4086 | 0.953 | 525.4 | 345.2 | 870.6 | 60.3 | 39.7 | 27800 | 0.1602 | 0.1642 | 0.1802 | 0.1963 | 0.0328 | 0.415 | 0.0957 | 734
Peacock | 605 | 24/7 | 0.4753 | 0.537 | 2 | 0.1588 | 0.1059 | 0.3177 | 0.953 | 570.1 | 208.7 | 778.8 | 73.2 | 26.8 | 21600 | 0.149 | 0.1532 | 0.1681 | 0.183 | 0.0319 | 0.418 | 0.0957 | 760
Squab | 605 | 26/7 | 0.4749 | 0.5522 | 2 | 0.1525 | 0.1186 | 0.3558 | 0.966 | 569.5 | 261.8 | 831.3 | 68.5 | 31.5 | 24300 | 0.1484 | 0.1524 | 0.1672 | 0.1821 | 0.0327 | 0.415 | 0.0953 | 764
Wood Duck | 605 | 30/7 | 0.4751 | 0.586 | 2 | 0.142 | 0.142 | 0.426 | 0.994 | 571.2 | 375.3 | 946.5 | 60.3 | 39.7 | 28900 | 0.1474 | 0.1512 | 0.1659 | 0.1806 | 0.0342 | 0.41 | 0.0944 | 773
Teal | 605 | 30/19 | 0.4751 | 0.5834 | 2 | 0.142 | 0.0852 | 0.426 | 0.994 | 571.2 | 367.4 | 938.6 | 60.9 | 39.1 | 30000 | 0.1475 | 0.1513 | 0.166 | 0.1808 | 0.0342 | 0.41 | 0.0944 | 773
Kingbird | 636 | 18/1 | 0.4997 | 0.5275 | 2 | 0.188 | 0.188 | 0.188 | 0.94 | 596.3 | 93.6 | 689.9 | 86.4 | 13.6 | 15700 | 0.1424 | 0.147 | 0.1612 | 0.1755 | 0.0304 | 0.424 | 0.0961 | 773
Swift | 636 | 36/1 | 0.4994 | 0.5133 | 3 | 0.1329 | 0.1329 | 0.1329 | 0.93 | 596 | 46.8 | 642.8 | 92.7 | 7.3 | 13800 | 0.143 | 0.1483 | 0.1676 | 0.1844 | 0.0301 | 0.425 | 0.0964 | 753
Goldfinch | 636 | 22/7 | 0.4994 | 0.5484 | 2 | 0.17 | 0.0944 | 0.2832 | 0.963 | 598.8 | 165.8 | 764.6 | 78.3 | 21.7 | 19800 | 0.1423 | 0.1466 | 0.1608 | 0.175 | 0.0319 | 0.418 | 0.0954 | 779
Rook | 636 | 24/7 | 0.4996 | 0.5643 | 2 | 0.1628 | 0.1085 | 0.3255 | 0.977 | 599.1 | 219.1 | 818.2 | 73.2 | 26.8 | 22600 | 0.1417 | 0.1458 | 0.16 | 0.1742 | 0.0327 | 0.415 | 0.095 | 784
Grosbeak | 636 | 26/7 | 0.4995 | 0.5808 | 2 | 0.1564 | 0.1216 | 0.3648 | 0.99 | 599 | 275.2 | 874.2 | 68.5 | 31.5 | 25200 | 0.1411 | 0.1451 | 0.1592 | 0.1733 | 0.0335 | 0.412 | 0.0946 | 789
Scoter | 636 | 30/7 | 0.4995 | 0.616 | 2 | 0.1456 | 0.1456 | 0.4368 | 1.019 | 600.5 | 394.6 | 995.1 | 60.3 | 39.7 | 30400 | 0.1402 | 0.1439 | 0.1579 | 0.1719 | 0.0351 | 0.407 | 0.0937 | 798
Egret | 636 | 30/19 | 0.4995 | 0.6135 | 2 | 0.1456 | 0.0874 | 0.437 | 1.019 | 600.5 | 386.7 | 987.2 | 60.8 | 39.2 | 31500 | 0.1403 | 0.144 | 0.158 | 0.172 | 0.0351 | 0.407 | 0.0937 | 797
Flamingo | 666.6 | 24/7 | 0.5238 | 0.5917 | 2 | 0.1667 | 0.1111 | 0.3333 | 1 | 628.2 | 229.7 | 857.9 | 73.2 | 26.8 | 23700 | 0.1352 | 0.1393 | 0.1528 | 0.1663 | 0.0335 | 0.412 | 0.0943 | 807
Gannet | 666.6 | 26/7 | 0.5234 | 0.6086 | 2 | 0.1601 | 0.1245 | 0.3735 | 1.014 | 627.7 | 288.5 | 916.2 | 68.5 | 31.5 | 26400 | 0.1347 | 0.1385 | 0.152 | 0.1654 | 0.0343 | 0.409 | 0.0939 | 812
Stilt | 715.5 | 24/7 | 0.5622 | 0.635 | 2 | 0.1727 | 0.1151 | 0.3453 | 1.036 | 674.2 | 246.6 | 920.8 | 73.2 | 26.8 | 25900 | 0.126 | 0.1299 | 0.1425 | 0.1551 | 0.0347 | 0.408 | 0.0932 | 844
Starling | 715.5 | 26/7 | 0.562 | 0.6535 | 2 | 0.1659 | 0.129 | 0.387 | 1.051 | 674 | 309.7 | 983.7 | 68.5 | 31.5 | 28400 | 0.1255 | 0.1292 | 0.1417 | 0.1543 | 0.0355 | 0.405 | 0.0928 | 849
Crow | 715.5 | 54/7 | 0.5619 | 0.6347 | 3 | 0.1151 | 0.1151 | 0.345 | 1.04 | 673.8 | 246.5 | 920.3 | 73.2 | 26.8 | 26000 | 0.126 | 0.1304 | 0.1474 | 0.1621 | 0.035 | 0.407 | 0.0932 | 827
Redwing | 715.5 | 30/19 | 0.5617 | 0.6897 | 2 | 0.1544 | 0.0926 | 0.463 | 1.081 | 675.3 | 434 | 1109.3 | 60.9 | 39.1 | 34600 | 0.1247 | 0.1282 | 0.1407 | 0.1531 | 0.0372 | 0.399 | 0.092 | 859
Coot | 795 | 36/1 | 0.6244 | 0.6417 | 3 | 0.1486 | 0.1486 | 0.1486 | 1.04 | 745.1 | 98.5 | 843.6 | 92.7 | 7.3 | 16800 | 0.1144 | 0.1194 | 0.1346 | 0.1478 | 0.0337 | 0.411 | 0.0931 | 866
Puffin | 795 | 22/7 | 0.6244 | 0.6857 | 2 | 0.1901 | 0.1056 | 0.3168 | 1.077 | 148.8 | 207.6 | 356.4 | 78.3 | 21.7 | 24800 | 0.1139 | 0.1179 | 0.1292 | 0.1405 | 0.0357 | 0.405 | 0.0921 | 895
Cuckoo | 795 | 24/7 | 0.6244 | 0.7053 | 2 | 0.182 | 0.1213 | 0.3639 | 1.092 | 748.8 | 273.9 | 1022.7 | 73.2 | 26.8 | 27900 | 0.1134 | 0.1172 | 0.1285 | 0.1398 | 0.0365 | 0.402 | 0.0917 | 901
Drake | 795 | 26/7 | 0.6247 | 0.7263 | 2 | 0.1749 | 0.136 | 0.408 | 1.108 | 149.1 | 344.3 | 493.4 | 68.5 | 31.5 | 31500 | 0.1129 | 0.1166 | 0.1278 | 0.1391 | 0.0374 | 0.399 | 0.0912 | 907
Skimmer | 795 | 30/7 | 0.6245 | 0.7702 | 2 | 0.1628 | 0.1628 | 0.4884 | 1.14 | 750.7 | 493.3 | 1244 | 60.3 | 39.7 | 37700 | 0.1121 | 0.1155 | 0.1267 | 0.1379 | 0.0392 | 0.393 | 0.0904 | 918
Macaw | 795 | 42/7 | 0.6246 | 0.6567 | 3 | 0.1376 | 0.0764 | 0.2292 | 1.055 | 749 | 108.6 | 857.6 | 87.3 | 12.7 | 20100 | 0.1146 | 0.1194 | 0.1345 | 0.1478 | 0.0346 | 0.408 | 0.0927 | 870
Tern | 795 | 45/7 | 0.6242 | 0.6674 | 3 | 0.1329 | 0.0886 | 0.2658 | 1.063 | 748.6 | 146.1 | 894.7 | 83.7 | 16.3 | 22100 | 0.1143 | 0.119 | 0.1341 | 0.1474 | 0.0352 | 0.406 | 0.0925 | 873
Condor | 795 | 54/7 | 0.624 | 0.7049 | 3 | 0.1213 | 0.1213 | 0.3639 | 1.092 | 148.4 | 273.9 | 422.3 | 73.2 | 26.8 | 28200 | 0.1134 | 0.1177 | 0.1328 | 0.1459 | 0.0368 | 0.401 | 0.0917 | 883
Mallard | 795 | 30/19 | 0.6245 | 0.7669 | 2 | 0.1628 | 0.0977 | 0.4885 | 1.14 | 750.7 | 483.2 | 1233.9 | 60.8 | 39.2 | 38400 | 0.1122 | 0.1156 | 0.1268 | 0.138 | 0.0392 | 0.393 | 0.0904 | 917
Ruddy | 900 | 45/7 | 0.7066 | 0.7555 | 3 | 0.1414 | 0.0943 | 0.2829 | 1.131 | 847.4 | 165.5 | 1012.9 | 83.7 | 16.3 | 24400 | 0.101 | 0.1055 | 0.1187 | 0.1304 | 0.0374 | 0.399 | 0.0906 | 943
Canary | 900 | 54/7 | 0.7069 | 0.7985 | 3 | 0.1291 | 0.1291 | 0.3873 | 1.162 | 847.7 | 310.2 | 1157.9 | 73.2 | 26.8 | 31900 | 0.1002 | 0.1043 | 0.1175 | 0.129 | 0.0392 | 0.393 | 0.0898 | 955
Corncrake | 954 | 20/7 | 0.7492 | 0.801 | 2 | 0.2184 | 0.0971 | 0.291 | 1.165 | 898.5 | 175.5 | 1074 | 83.7 | 16.3 | 25600 | 0.0953 | 0.0994 | 0.1088 | 0.1183 | 0.0381 | 0.396 | 0.0897 | 996
Redbird | 954 | 24/7 | 0.7495 | 0.8466 | 2 | 0.1994 | 0.1329 | 0.399 | 1.196 | 8938.8 | 328.7 | 9267.5 | 73.2 | 26.8 | 33500 | 0.0945 | 0.0982 | 0.1076 | 0.117 | 0.04 | 0.391 | 0.089 | 1009
Phoenix | 954 | 42/7 | 0.7491 | 0.7877 | 3 | 0.1507 | 0.0837 | 0.2511 | 1.155 | 898.4 | 130.4 | 1028.8 | 87.3 | 12.7 | 23400 | 0.0955 | 0.1002 | 0.1126 | 0.1235 | 0.0379 | 0.397 | 0.09 | 974
Rail | 954 | 45/7 | 0.7492 | 0.801 | 3 | 0.1456 | 0.0971 | 0.2913 | 1.165 | 898.5 | 173.5 | 1072 | 83.7 | 16.3 | 25900 | 0.0953 | 0.0998 | 0.1122 | 0.1231 | 0.0385 | 0.395 | 0.0897 | 978
Cardinal | 954 | 54/7 | 0.7491 | 0.8462 | 3 | 0.1329 | 0.1329 | 0.3987 | 1.196 | 898.3 | 328.7 | 1227 | 73.2 | 26.8 | 33800 | 0.0945 | 0.0986 | 0.111 | 0.1218 | 0.0404 | 0.39 | 0.089 | 990
Canvasback | 954 | 30/19 | 0.7491 | 0.9199 | 2 | 0.1783 | 0.107 | 0.535 | 1.248 | 900.5 | 79.6 | 980.1 | 60.8 | 39.2 | 46100 | 0.0935 | 0.0968 | 0.106 | 0.1153 | 0.043 | 0.382 | 0.0877 | 1027
Snowbird | 1033.5 | 42/7 | 0.8121 | 0.8539 | 3 | 0.1569 | 0.0872 | 0.2616 | 1.203 | 973.9 | 141.5 | 1115.4 | 87.3 | 12.7 | 25400 | 0.0881 | 0.0929 | 0.1042 | 0.1142 | 0.0395 | 0.392 | 0.0888 | 1024
Ortolan | 1033.5 | 45/7 | 0.8112 | 0.8673 | 3 | 0.1515 | 0.101 | 0.303 | 1.212 | 972.8 | 189.9 | 1162.7 | 83.7 | 16.3 | 27700 | 0.0879 | 0.0925 | 0.1038 | 0.1138 | 0.0401 | 0.39 | 0.0886 | 1028
Curlew | 1033.5 | 54/7 | 0.8112 | 0.9164 | 3 | 0.1383 | 0.1383 | 0.4149 | 1.245 | 972.8 | 356 | 1328.8 | 73.2 | 26.8 | 36600 | 0.0872 | 0.0913 | 0.1026 | 0.1126 | 0.042 | 0.385 | 0.0878 | 1041
Avocet | 1113 | 42/7 | 0.8743 | 0.9192 | 3 | 0.1628 | 0.0904 | 0.2712 | 1.248 | 1048.5 | 152.1 | 1200.6 | 87.3 | 12.7 | 27100 | 0.0818 | 0.0866 | 0.0971 | 0.1063 | 0.041 | 0.388 | 0.0877 | 1072
Bluejay | 1113 | 45/7 | 0.8745 | 0.935 | 3 | 0.1573 | 0.1049 | 0.3147 | 1.259 | 1048.7 | 204.8 | 1253.5 | 83.7 | 16.3 | 29800 | 0.0816 | 0.0862 | 0.0967 | 0.1059 | 0.0416 | 0.386 | 0.0874 | 1076
Finch | 1113 | 54/19 | 0.8746 | 0.9855 | 3 | 0.1436 | 0.0862 | 0.4314 | 1.293 | 1053.9 | 376.1 | 1430 | 73.7 | 26.3 | 39100 | 0.0814 | 0.0855 | 0.096 | 0.1052 | 0.0436 | 0.38 | 0.0867 | 1088
Oxbird | 1192.5 | 42/7 | 0.9366 | 0.9847 | 3 | 0.1685 | 0.0936 | 0.2808 | 1.292 | 1123.2 | 163.1 | 1286.3 | 87.3 | 12.7 | 29000 | 0.0764 | 0.0812 | 0.0909 | 0.0995 | 0.0424 | 0.383 | 0.0867 | 1118
Bunting | 1192.5 | 45/7 | 0.9367 | 1.0014 | 3 | 0.1628 | 0.1085 | 0.3255 | 1302 | 1123.4 | 219.1 | 1342.5 | 83.7 | 16.3 | 32000 | 0.0762 | 0.0808 | 0.0905 | 0.0991 | 0.0431 | 0.382 | 0.0864 | 1123
Grackle | 1192.5 | 54/19 | 0.9365 | 1.0552 | 3 | 0.1486 | 0.0892 | 0.446 | 1.337 | 1128.6 | 402.8 | 1531.4 | 73.7 | 26.3 | 41900 | 0.076 | 0.0801 | 0.0898 | 0.0984 | 0.0451 | 0.376 | 0.0856 | 1135
Scissortail | 1272 | 42/7 | 0.9987 | 4.0501 | 3 | 0.174 | 0.0967 | 0.2901 | 1.334 | 1197.7 | 174 | 1371.7 | 87.3 | 12.7 | 30900 | 0.0716 | 0.0765 | 0.0855 | 0.0935 | 0.0438 | 0.38 | 0.0857 | 1163
Bittern | 1272 | 45/7 | 0.9987 | 1.0678 | 3 | 0.1681 | 0.1121 | 0.3363 | 61.345 | 1197.7 | 233.9 | 1431.6 | 83.7 | 16.3 | 34100 | 0.0714 | 0.0761 | 0.0851 | 0.0931 | 0.0445 | 0.378 | 0.0855 | 1168
Pheasant | 1272 | 54/19 | 0.9993 | 1.1259 | 3 | 0.1535 | 0.0921 | 0.4605 | 1.382 | 1204.3 | 429.4 | 1633.7 | 73.7 | 26.3 | 43600 | 0.0712 | 0.0754 | 0.0844 | 0.0924 | 0.0466 | 0.372 | 0.0847 | 1181
Dipper | 1351.5 | 45/7 | 1.0614 | 1.1347 | 3 | 0.1733 | 0.1155 | 0.3465 | 1.386 | 1272.9 | 248.3 | 1521.2 | 83.7 | 16.3 | 36200 | 0.0672 | 0.072 | 0.0804 | 0.0879 | 0.0459 | 0.374 | 0.0846 | 1212
Martin | 1351.5 | 54/19 | 1.0614 | 1.1958 | 3 | 0.1582 | 0.0949 | 0.4745 | 1.424 | 1279.1 | 455.9 | 1735 | 73.7 | 26.3 | 46300 | 0.0671 | 0.0712 | 0.0797 | 0.0872 | 0.048 | 0.368 | 0.0838 | 1226
Bobolink | 1431 | 45/7 | 1.1236 | 1.2013 | 3 | 0.1783 | 0.1189 | 0.3567 | 1.427 | 1347.5 | 263.1 | 1610.6 | 83.7 | 16.3 | 38300 | 0.0635 | 0.0684 | 0.0762 | 0.0833 | 0.0472 | 0.371 | 0.0837 | 1255
Plover | 1431 | 54/19 | 1.1241 | 4.2665 | 3 | 0.1628 | 0.0977 | 0.4885 | 1.465 | 1354.6 | 433.2 | 1787.8 | 73.7 | 26.3 | 49100 | 0.0633 | 0.0675 | 0.0755 | 0.0825 | 0.0494 | 0.365 | 0.0829 | 1269
Nuthatch | 1510.5 | 45/7 | 1.1862 | 1.2682 | 3 | 0.1832 | 0.1221 | 0.3663 | 1.466 | 1422.5 | 270.5 | 1693 | 83.7 | 16.3 | 40000 | 0.0602 | 0.0651 | 0.0725 | 0.0791 | 0.0485 | 0.367 | 0.0829 | 1296
Parrot | 1510.5 | 54/19 | 1.1856 | 1.3357 | 3 | 0.1672 | 0.1003 | 0.5016 | 1.505 | 1428.8 | 909.2 | 2338 | 73.7 | 26.3 | 51700 | 0.06 | 0.0643 | 0.0717 | 0.0784 | 0.0508 | 0.362 | 0.0821 | 1312
Lapwing | 1590 | 45/7 | 1.2492 | 4.3355 | 3 | 0.188 | 0.1253 | 0.3759 | 1.504 | 1498.1 | 292.2 | 1790.3 | 83.7 | 16.3 | 42200 | 0.0572 | 0.0622 | 0.0692 | 0.0754 | 0.0497 | 0.364 | 0.0822 | 1337
Falcon | 1590 | 54/19 | 1.2489 | 1.4072 | 3 | 0.1716 | 0.103 | 0.515 | 1.545 | 1505 | 937 | 2442 | 73.7 | 26.3 | 54500 | 0.057 | 0.0613 | 0.0684 | 0.0747 | 0.0521 | 0.359 | 0.0814 | 1353
Chukar | 1780 | 84/19 | 1.3986 | 1.5126 | 4 | 0.1456 | 0.0874 | 0.437 | 1.602 | 1685.4 | 386.7 | 2072.1 | 81.3 | 18.7 | 51000 | 0.0512 | 0.0561 | 0.0609 | 0.0658 | 0.0534 | 0.355 | 0.0803 | 1453
Mockingbird | 2034.5 | 72/7 | 1.5979 | 1.6671 | 4 | 0.1681 | 0.1122 | 0.336 | 1.681 | 1925.7 | 234.3 | 2160 | 89.2 | 10.8 | 46800 | 0.045 | 0.0509 | 0.0551 | 0.0593 | 0.0553 | 0.351 | 0.0789 | 1551
Roadrunner | 2057 | 76/19 | 1.6152 | 1.7032 | 4 | 0.1645 | 0.0768 | 0.384 | 1.7 | 1946.5 | 298.6 | 2245.1 | 86.7 | 13.3 | 50400 | 0.0445 | 0.0502 | 0.0543 | 0.0585 | 0.0562 | 0.349 | 0.0785 | 1567
Bluebird | 2156 | 84/19 | 1.6931 | 1.8309 | 4 | 0.1602 | 0.0961 | 0.4805 | 1.762 | 2040.4 | 467.5 | 2507.9 | 81.4 | 18.6 | 60300 | 0.0423 | 0.0477 | 0.0516 | 0.0555 | 0.0588 | 0.344 | 0.0775 | 1622
Kiwi | 2167 | 72/7 | 1.7022 | 1.7758 | 4 | 0.1735 | 0.1157 | 0.3474 | 1.735 | 2051.4 | 249.2 | 2300.6 | 89.2 | 10.8 | 49800 | 0.0423 | 0.0484 | 0.0523 | 0.0562 | 0.057 | 0.348 | 0.0779 | 1607
Thrasher | 2312 | 76/19 | 1.8155 | 1.9144 | 4 | 0.1744 | 0.0814 | 0.407 | 1.802 | 2187.9 | 335.4 | 2523.3 | 86.7 | 13.3 | 56700 | 0.0396 | 0.0457 | 0.0493 | 0.0529 | 0.0595 | 0.342 | 0.0768 | 1672
Joree | 2515 | 76/19 | 1.975 | 2.0826 | 4 | 0.1819 | 0.0849 | 0.4245 | 1.88 | 2380.1 | 364.9 | 2745 | 86.7 | 13.3 | 61700 | 0.0364 | 0.0428 | 0.046 | 0.0493 | 0.0621 | 0.337 | 0.0755 | 1751
Notes
(1) Data based on a nominal conductor manufactured in accordance with ASTM B232.
(2) Resistance and ampacity based on an aluminum conductivity of 61.2% IACS at 20°C and a steel conductivity of 8% IACS at 20°C.
(3) AC resistance of designs with three layers of aluminum will differ based on current density and therefore input conditions.
(4) Ampacity based on 25°C ambient temperature, 2 ft/s perpendicular wind, 0.5 emissivity, 0.5 absorptivity, 60 Hz, clear atmosphere, sea level, 30° N latitude, N-S line azimuth, noon on June 10th.
(5) RBS is based on Class A galvanized steel core wire in accordance with ASTM B498.
Source file: ACSR.pdf (uploaded scan)